## Sheet1
ITEM CODE | SR. NO. | LABEL LIST | TYPE REFERENCE | DESCRIPTION | MAKE | CAT NO. | ICOG PANEL | TOTAL QTY 2 SETS
SB202-C2DC | 1 | CLS CKT 2A A1-01 | A1-01 | 2 POLE, 2A, MCB FOR CLOSE CIRCUIT,110V DC. | ABB | SB202-C2DC | 1 | 2
SB202-C2DC | 2 | IND CKT 2A A1-05 | A1-05 | 2 POLE, 2A, MCB FOR INDICATION CIRCUIT, 110V DC. | ABB | SB202-C2DC | 1 | 2
SB202-C2DC | 3 | ANN CKT 2A A1-07 | A1-07 | 2 POLE, 2A, MCB FOR ANNUNCIATOR CIRCUIT, 110V DC. | ABB | SB202-C2DC | 1 | 2
SB202M-C2 | 4 | ANN CKT 2A A1-08 | A1-08 | 2 POLE, 2A, MCB FOR ANNUNCIATOR CIRCUIT, 230V AC. | ABB | SB202M-C2 | 1 | 2
4A_HRC_CARTRIDGE | 5 | R PH 4A A1-13 | A1-13 | P.T. FUSES 4A ,FOR PT SECONDARY R-PAHSE CORE-I | L&T | 4A_HRC | 1 | 2
4A_HRC_CARTRIDGE | 6 | Y PH 4A A1-14 | A1-14 | P.T. FUSES 4A ,FOR PT SECONDARY Y-PHASE CORE-I | L&T | 4A_HRC | 1 | 2
4A_HRC_CARTRIDGE | 7 | B PH 4A A1-15 | A1-15 | P.T. FUSES 4A ,FOR PT SECONDARY B-PHASE CORE-I | L&T | 4A_HRC | 1 | 2
SHORTING_LINK | 8 | N LINK A1-16 | A1-16 | SHORTING LINK PT SECONDARY NEUTRAL CORE-I | REPUTED | SHORTING_LINK | 1 | 2
4A_HRC_CARTRIDGE | 9 | R PH 4A A1-17 | A1-17 | P.T. FUSES 4A ,FOR PT SECONDARY R-PAHSE CORE-II | L&T | 4A_HRC | 1 | 2
4A_HRC_CARTRIDGE | 10 | Y PH 4A A1-18 | A1-18 | P.T. FUSES 4A ,FOR PT SECONDARY Y-PHASE CORE-II | L&T | 4A_HRC | 1 | 2
4A_HRC_CARTRIDGE | 11 | B PH 4A A1-19 | A1-19 | P.T. FUSES 4A ,FOR PT SECONDARY B-PHASE CORE-II | L&T | 4A_HRC | 1 | 2
SHORTING_LINK | 12 | N LINK A1-20 | A1-20 | SHORTING LINK PT SECONDARY NEUTRAL CORE-II | REPUTED | SHORTING_LINK | 1 | 2
HRC_CARTRIDGE_BASE | [7 empty] | 16
SB202M-C2 | 13 | MOT CKT 2A B10-01 | B10-01 | 2 POLE, 2A, AC MCB FOR MOTOR CIRCUIT, 230V AC. | ABB | SB202M-C2 | 1 | 2
SB202-C6DC | 14 | DC CKT 6A B10-02 | B10-02 | 2 POLE, 6A, AC MCB FOR DC AUXILARY CIRCUIT, 110V DC. | ABB | SB202-C6DC | 1 | 2
SB202M-C6 | 15 | UPS CKT 6A B10-03 | B10-03 | 2 POLE, 6A, AC MCB FOR UPS AC AUXILIARY CIRCUIT, 230V AC. | ABB | SB202M-C6 | 1 | 2
SB202M-C6 | 16 | RAW CKT 6A B10-03A | B10-03A | 2 POLE, 6A, AC MCB FOR RAW AC AUXILIARY CIRCUIT, 230V AC. | ABB | SB202M-C6 | 1 | 2
5PIN-SOCKET-3SW-PRE | 1 | SOCKET A3-01 | A3-01 | COMBINE SWITCH BOX WITH 3NOS. SWITCHES AND 1 NO. 5-PIN SOCKET, 230V AC. SWITCH-1 FOR ILLUMINATION LAMP, SWITCH-2 FOR SPACE HEATER, SWITCH-3 FOR 5-PIN SOCKET. | PRESSFIT | 5PIN-SOCKET-2SW-PRE | 1 | 2
5A-5PIN-SOCKET-PRE | [7 empty] | 2
SW-THERMOSTAT-20A-230V | 1 | THERMOSTAT B10-04,04A,04B,04C | B10-04 | THERMOSTAT, SETTING: 0-75 DEG. CEN. 20A, 230V AC. | APT CONTROL | _ | 4 | 8
5W-LEDLAMP | 1 | - | B10-07 | ILLUMININATION LED LAMP 5W, AUX. VOLTAGE: 230V AC. | WIPRO | 5W-LEDLAMP | 1 | 2
BABY-HOLDER | [7 empty] | 2
TS-PP-230/110VDC 30 MINUTES | 1 | - | B10-16 | POWER PACK UNIT INPUT: 230V AC, OUTPUT: 110V DC, BATTERY BACK UP: 30 MINUTES. 10AH BATTERY. | TECHNOCRAFTS | _ | 1 | 2
KLTDM4 | 1 | _ | B50-01 | DISCONNECTING TYPE TERMINAL BLOCK. | ELMEX | _ | 45 | 90
KUT6 | 2 |  | B50-02 | NON-DISCONNECTING TYPE TERMINAL BLOCK. | ELMEX |  | 214 | 428
KPLD4 | 3 |  | B50-03 | END PLATE FOR DISCONNECTING TYPE TERMINAL BLOCK. | ELMEX |  | 5 | 10
KPX | 4 |  | B50-04 | END PLATE FOR NON-DISCONNECTING TYPE TERMINAL BLOCK. | ELMEX |  | 10 | 20
SCKN | 5 |  | B50-05 | END CLAMP WITH SCREW. | ELMEX |  | 15 | 30
CR-M110DC2 | 1 | SP. CHG B10-09 | B10-09 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 2 C/O S/R, AUX. VOLTAGE: 110V DC, FOR SPRING CHARGE CIRCUIT. | ABB | CR-M110DC2 | 1 | 2
CR-M110DC2 | 2 | A/P RLY B10-10 | B10-10 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 2 C/O S/R, AUX. VOLTAGE: 110V DC, FOR ANTIPUMPING CIRCUIT (94). | ABB | CR-M110DC2 | 1 | 2
CR-M110DC2 | 3 | DC FAIL CKT B10-11 | B10-11 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 2 C/O S/R, AUX. VOLTAGE: 110V DC, FOR DC CIRCUIT FAIL (80D). | ABB | CR-M110DC2 | 1 | 2
CR-M230AC2 | 4 | AC FAIL CKT B10-12 | B10-12 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 2 C/O S/R, AUX. VOLTAGE: 230V AC, FOR AC CIRCUIT FAIL (80A). | ABB | CR-M230AC2 | 1 | 2
CR-M230AC2 | 5 | AC UPS HEALTHY B10-12A | B10-12A | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 2 C/O S/R, AUX. VOLTAGE: 230V AC, FOR AC UPS HEALTHY (80A). | ABB | CR-M230AC2 | 1 | 2
CR-M024DC2 | 6 | CB CLS B10-13 | B10-13 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 2 C/O S/R, AUX. VOLTAGE: 24V DC, FOR CIRCUIT BREAKER CLOSE SIGNAL FROM SCADA | ABB | CR-M024DC2 | 1 | 2
CR-M024DC2 | 7 | CB TRIP B10-14 | B10-14 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 2 C/O S/R, AUX. VOLTAGE: 24V DC, FOR CIRCUIT BREAKER TRIP SIGNAL FROM SCADA | ABB | CR-M024DC2 | 1 | 2
CS94029-1000 | 8 | CB CONT MUL B10-15 | B10-15 | AUXILIARY CONTACTOR WITH CONTACTS: 2NO + 2NC AUX. VOLTAGE: 110V DC, FOR BREAKER CONTACT MULTIPLIER. | L&T | - | 1 | 2
CR-M110DC4 | 9 | ES CONT MUL B10-15A | B10-15A | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 4 C/O S/R, AUX. VOLTAGE: 110V DC, FOR ES CONTACT MULTIPLIER | ABB | CR-M110DC4 | 1 | 2
CR-M110DC4 | 10 | BUCH. TRIP B10-17 | B10-17 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 4 C/O S/R, AUX. VOLTAGE: 110V DC, FOR (BUCHHOLZ) # TRIP (63T). | ABB | CR-M110DC4 | 1 | 2
CR-M110DC2 | 11 | BUCH. ALR B10-18 | B10-18 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 2 C/O S/R, AUX. VOLTAGE: 110V DC, FOR (BUCHHOLZ) # ALARM (63A). | ABB | CR-M110DC2 | 1 | 2
CR-M110DC4 | 12 | OT TRIP B10-19 | B10-19 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 4 C/O S/R, AUX. VOLTAGE: 110V DC, FOR (OIL TEMP. HIGH) # TRIP (26T). | ABB | CR-M110DC4 | 1 | 2
CR-M110DC2 | 13 | OT ALR B10-20 | B10-20 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 2 C/O S/R, AUX. VOLTAGE: 110V DC, FOR (OIL TEMP. HIGH) # ALARM (26A). | ABB | CR-M110DC2 | 1 | 2
CR-M110DC4 | 14 | WDG. TRIP B10-21 | B10-21 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 4 C/O S/R, AUX. VOLTAGE: 110V DC, FOR (HV WDG TEMP. HIGH) # TRIP (49T). | ABB | CR-M110DC4 | 1 | 2
CR-M110DC2 | 15 | WDG. ALR B10-22 | B10-22 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 2 C/O S/R, AUX. VOLTAGE: 110V DC, FOR (HV WDG TEMP. HIGH) # ALARM (49A). | ABB | CR-M110DC2 | 1 | 2
CR-M110DC4 | 16 | LV-1 WDG. TRIP B10-23 | B10-23 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 4 C/O S/R, AUX. VOLTAGE: 110V DC, FOR (LV WDG TEMP. HIGH) # TRIP-1 (49T-1). | ABB | CR-M110DC4 | 1 | 2
CR-M110DC2 | 17 | LV-1 WDG. ALR B10-24 | B10-24 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 2 C/O S/R, AUX. VOLTAGE: 110V DC, FOR (LV WDG TEMP. HIGH) # ALARM-1 (49A-1). | ABB | CR-M110DC2 | 1 | 2
CR-M110DC4 | 18 | LV-2 WDG. TRIP B10-25 | B10-25 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 4 C/O S/R, AUX. VOLTAGE: 110V DC, FOR (LV WDG TEMP. HIGH) # TRIP-2 (49T-2). | ABB | CR-M110DC4 | 1 | 2
CR-M110DC2 | 19 | LV-2 WDG. ALR B10-26 | B10-26 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 2 C/O S/R, AUX. VOLTAGE: 110V DC, FOR (LV WDG TEMP. HIGH) # ALARM-2 (49A-2). | ABB | CR-M110DC2 | 1 | 2
CR-M110DC4 | 20 | PRV TRIP B10-27 | B10-27 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 4 C/O S/R, AUX. VOLTAGE: 110V DC, FOR FOR PRV TRIP (63X-1) | ABB | CR-M110DC4 | 1 | 2
CR-M110DC2 | 21 | MOG ALR B10-28 | B10-28 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 2 C/O S/R, AUX. VOLTAGE: 110V DC, FOR FOR MOG ALARM (63X-2) | ABB | CR-M110DC2 | 1 | 2
CR-M110DC4 | 22 | SPARE TRIP B10-29 | B10-29 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 4 C/O S/R, AUX. VOLTAGE: 110V DC, FOR FOR SPARE TRIP (63X-3) | ABB | CR-M110DC4 | 1 | 2
CR-M110DC2 | 23 | SPARE ALR B10-30 | B10-30 | TYPE: CRM, SINGLE ELEMENT AUX. RELAY WITH CONTACTS: 2 C/O S/R, AUX. VOLTAGE: 110V DC, FOR FOR SPARE ALARM (63X-4) | ABB | CR-M110DC2 | 1 | 2
CR-M2SS | [7 empty] | 28
CR-M4SS | [7 empty] | 16
HBFFAEAGNBA1BNA11G | 24 | PROT RLY D5-04 | D5-04 | TYPE: REF 615, NUMERICAL MULTIFUNCTION RELAY, FUNCTIONS: (50+51+50N+51N+27+59+95-1+60), FLUSH MOUNTING, CONTACTS : 16 BI + 10 BO, AUX. VOLTAGE: 110V DC, In: 1A. WITH IEC 61850 PROTOCOL WITH RJ45 PORT. | ABB | HBFFAEAGNBA1BNA11G | 1 | 2
PQ8NCH2J-110-5-2 | 25 | TRIP RLY D5-10 | D5-10 | TYPE: PQ8nCH2J, TRIPPING RELAY, (86), FLUSH MOUNTING, CASE SIZE: 1/2, CONTACTS: 5NO+2NC HR, WITH HR FLAG ON EACH ELEMENT, AUX. VOLTAGE: 110V DC. | ABB | PQ8nCH2J | 1 | 2
TCS-110 | 26 | TCS RLY D5-12 | D5-12 | TYPE: TCS,(95-2), TRIP CIRCUIT SUPERVISION RELAY, NON-DRAWOUT, FLUSH MOUNTING, CASE SIZE 1/2, CONTACTS: 1NO+1NC+2C/O SR, AUX. VOLTAGE: 110V DC. | ABB | TCS -2 | 1 | 2
SE-3PH-3A-0.5 | 1 | DIG. AMM D5-21 | D5-21 | DIGITAL AMMETER, WITH BUILT IN SELECTOR SWITCH CTR: PROGRAMMABLE, In: 1A, AUX. VOLTAGE: 110V DC, ACC CLASS: 0.5, SIZE: 96mmx96mm. | SECURE | SE-3PH-3A-0.5 | 1 | 2
SE-3PH-3V-0.5 | 2 | DIG.VOLT D5-22 | D5-22 | DIGITAL VOLTMETER, WITH BUILT IN SELECTOR SWITCH, PTR: 33kV/110V AC, AUX. VOLTAGE: 110V DC, ACC CLASS: 0.5, SIZE: 96mmx96mm. | SECURE | SE-3PH-3V-0.5 | 1 | 2
SE-TVM-PREMIER300-0.2S-RS485-200/1A-33KV/R3/110V/R3-JK | 3 | TVM D5-27 | D5-27 | DIGITAL TRIVECTOR METER, MODEL-PREMIER 300, 3 PHASE, 4 WIRE, 3 ELEMENT SYSTEM,CTR: 200 /1A, PTR: 33kV/R3/110V/R3 ,CLASS : 0.2S, WITH MODBUS PROTOCOL-RS485 PORT, STATE-JHARKHAND | SECURE | - | 1 | 2
BCA02P006K144 | 1 | TNC S/W D5-33 | D5-33 | BREAKER CONTROL SWITCH, LABEL: TRIP-NEUTRAL-CLOSE, (52CS), 3 POSITION, 4 WAYS, SPRING RETURN TO NEUTRAL, PISTOL GRIP HANDLE, ANGULAR MOVEMENT: 45 DEG. SIZE: 72.5x72.5 mm, CONTACTS: 2C, 2T, 25A. | KAYCEE | BCA02P006K144 | 1 | 2
BCE02T009A220 | 2 | LR S/W D5-34 | D5-34 | LOCAL REMOTE SELECTOR SWITCH, LABEL: LOCAL-REMOTE, (52LR) STAYPUT, 2 POLE, 4 WAY, WING TYPE KNOB, LOCKABLE TYPE, ANGULAR MOVEMENT: 90 DEG., SIZE: 95x95 mm., 2 CONTACT TO CLOSE IN EACH POSITION. 16A | KAYCEE | BCE02T009A220 | 1 | 2
EPLR110D | 1 | CB ON D5-41 | D5-41 | LED LAMP, RED COLOUR LENS, SUITABLE FOR 110V DC, BREAKER ON. | L&T | EPLR110D | 1 | 2
EPLG110D | 2 | CB OFF D5-42 | D5-42 | LED LAMP, GREEN COLOUR LENS, SUITABLE FOR 110V DC, BREAKER OFF. | L&T | EPLG110D | 1 | 2
EPLA110D | 3 | AUTO TRIP D5-43 | D5-43 | LED LAMP, AMBER COLOUR LENS, SUITABLE FOR 110V DC, AUTO TRIP. | L&T | EPLA110D | 1 | 2
EPLW110D | 4 | TCS HEALTHY-1 D5-44 | D5-44 | LED LAMP, WHITE COLOUR LENS, SUITABLE FOR 110V DC, TRIP CIRCUIT HEALTHY-1 | L&T | EPLW110D | 1 | 2
EPLW110D | 5 | TCS HEALTHY-2 D5-45 | D5-45 | LED LAMP, WHITE COLOUR LENS, SUITABLE FOR 110V DC, TRIP CIRCUIT HEALTHY-2 | L&T | EPLW110D | 1 | 2
EPLR064C | 6 | R PHASE D5-47 | D5-47 | LED LAMP, RED COLOUR LENS, SUITABLE FOR 63.5V AC R-PHASE HEALTHY. | L&T | EPLR064C | 1 | 2
EPLY064C | 7 | Y PHASE D5-48 | D5-48 | LED LAMP, YELLOW COLOUR LENS, SUITABLE FOR 63.5V AC Y-PHASE HEALTHY. | L&T | EPLY064C | 1 | 2
EPLB064C | 8 | B PHASE D5-49 | D5-49 | LED LAMP, BLUE COLOUR LENS, SUITABLE FOR 63.5V AC B-PHASE HEALTHY. | L&T | EPLB064C | 1 | 2
EPLB110D | 9 | SP. CHG D5-50 | D5-50 | LED LAMP, BLUE COLOUR LENS, SUITABLE FOR 110V DC, SPRING CHARGE. | L&T | EPLB110D | 1 | 2
EPLG110D | 10 | CB. TEST D5-51 | D5-51 | LED LAMP, GREEN COLOUR LENS, SUITABLE FOR 110V DC, BREAKER IN TEST. | L&T | EPLG110D | 1 | 2
EPLR110D | 11 | CB. SERV D5-52 | D5-52 | LED LAMP, RED COLOUR LENS, SUITABLE FOR 110V DC, BREAKER IN SERVICE. | L&T | EPLR110D | 1 | 2
EPLR240A | 12 | DC FAIL D5-53 | D5-53 | LED LAMP, RED COLOUR LENS, SUITABLE FOR 230V AC, FOR DC FAIL. | L&T | EPLR240C | 1 | 2
EPLR110D | 13 | AC FAIL D5-54 | D5-54 | LED LAMP, RED COLOUR LENS, SUITABLE FOR 110V DC, FOR AC FAIL. | L&T | EPLR110D | 1 | 2
EPLR110D | 14 | ES ON D5-55 | D5-55 | LED LAMP, RED COLOUR LENS, SUITABLE FOR 110V DC, FOR ES ON. | L&T | EPLR110D | 1 | 2
EPLG110D | 15 | ES OFF D5-56 | D5-56 | LED LAMP, GREEN COLOUR LENS, SUITABLE FOR 110V DC, FOR ES OFF. | L&T | EPLG110D | 1 | 2
EPLR240A | 16 | UPS HEALTHY D5-57 | D5-57 | LED LAMP, RED COLOUR LENS, SUITABLE FOR 230V AC, FOR UPS SUPPLY HEALTHY. | L&T | EPLR240C | 1 | 2
DAV-TTB-3PH-4WI | 1 | MTTB D5-60 | D5-60 | TEST TERMINAL BLOCK SUITABLE FOR 3 ELEMENT, 3 PHASE, 4 WIRE SYSTEM WITH REAR CONNECTION (FOR METERING). | DAV | DAV-TTB-3PH-4WI | 1 | 2
DAV-RTTB | 2 | RTTB D5-61 | D5-61 | TEST TERMINAL BLOCK SUITABLE FOR 3 ELEMENT, 3 PHASE, 4 WIRE SYSTEM WITH REAR CONNECTION (FOR PROTECTION) | DAV | DAV-RTTB | 2 | 4
EMNRMH1 | 3 | EM.PB D5-62 | D5-62 | PUSH BUTTON, MUSHROOM HEAD TYPE, STAYPUT, RED COLOUR WITH 4NO+1NC ELEMENT FOR EMERGENCY TRIP, PRESS TO LOCK & TWIST TO RELEASE. | L&T | EMNRMH1 | 1 | 2
EC1C-1NO | [7 empty] | 8
EC2C-1NC | [7 empty] | 4
AL-AN-24W-88-285V-RS485-WI-ADF | 1 | ANNUNCIATOR D5-71 | D5-71 | 24-WINDOW ALARM ANNUNCIATOR (30),WITH AC FAIL&DC FAIL ,FOR BOTH TRIP & NONTRIP ALARM, WITH BUILT IN, ACCEPT, MUTE, RESET, TEST PUSH BUTTONS, SOURCE I :AUX. VOLTAGE: 110V DC, SOURCE II:AUX. VOLTAGE: 230V AC. MODBUS PROTOCOL WITH RS485 PORT. | ALAN | AL-AN-24W-88-285V-RS485-WI-ADF | 1 | 2
AL-HOO-AUH-01 | 2 | HOOTER D5-72 | D5-72 | TWO TONE HOOTER, AUX. VOLTAGE: 110V DC, SIZE 96X96mm. | ALAN | AL-HOO-AUH-01 | 1 | 2
AL-HOO-AUH-01 | 3 | HOOTER D5-72A | D5-72A | TWO TONE HOOTER, AUX. VOLTAGE: 230V AC, SIZE 96X96mm. | ALAN | AL-HOO-AUH-01 | 1 | 2
VD4 361231.5-DRAW-OUT | 1 | _ | F01-01 | 33kV,1250A, 31.5kA/3SEC, VD4 BREAKER (52), OPERATION COUNTER. DRAWOUT TYPE, 58 PIN PLUG & SOCKET, FOR BREAKER CONTROL & AUX. CIRCUIT WIRING. 1. CLOSE AND TRIP COIL: 110V DC 2. ADDITIONL TRIP COIL: 110V DC 3. SPRING CHARGE MOTOR: 230V AC, 4. MECHANICAL ON/OFF INDICATOR, 5. MECHANICAL ON/OFF PUSH BUTTON, 6. SAFETY SHUTTER. 7. MECHANICAL OPERATION COUNTER 8. SPRING CHARGING HANDLE | ABB | VD4-331231.5-DRAW-OUT | 1 | 2
| 1 | _ | F01-02 | 33kV EARTH SWITCH 25kA/1SEC, WITH AUX. CONTACT: (2NO+2NC) | TECHNOCRAFTS | _ | 1 | 2
| 1 | _ | F02 | P.T HANDLING TROLLY | TECHNOCRAFTS | _ | 1 | 2
PR-PT-33-3C-50/0.2-50/3P-50/3P-F-INSULATION-CLASS-F | 2 | _ | F02-01,02,03 | 33kV SINGLE PHASE, CAST RESIN PT RATIO: 33kV/RT3/110V/RT3/110V/RT3/110V/3, CORE 1: BURDEN: 50VA, CLASS: 0.2, CORE 2: BURDEN: 50VA, CLASS: 3P, CORE 3: BURDEN: 50VA, CLASS: 3P FIXED TYPE, VOLTAGE FACTOR 1.2 CONTINUOUS & 1.9 FOR 8 HOURS. INSULATION CLASS: F | PRAGATI | - | 3 | 6
PT-FUSE-33KV | 4 | _ | F02-05,06,07 | P.T. FUSES 3.15A, 33kV. | PHOENIX | PT-FUSE-33KV | 3 | 6
PT-RES-250WATTS-150OHMS | 5 | _ | F02-09 | RESISTOR, 150 OHM, 250W USED FOR DELTA CONNECTED PT. | K2 | PT-RES-250WATTS-150-OHMS | 1 | 2
PR-CT-200-4106-01 | 1 | _ | F03-01,02,03 | 33kV SINGLE PHASE, CAST RESIN CURRENT TRANSFORMER, CTR: 200/1-1-1A, CORE 1: BURDEN: 10VA, CLASS: 0.2S, ISF<=5, CORE 2: BURDEN: 10VA, CLASS: 5P20, CORE 3: BURDEN: 10VA, CLASS: 5P20, STC: 26.3kA/1SEC, CT SECONDARY TERMINAL ON P1 SIDE, WOUND TYPE, INSULATION CLASS: F | PRAGATI | - | 3 | 6
OCP2-29M | 1 | _ | F04-01,02,03 | SURGE ARRESTOR 36.25kV, 10kA,MCOV-29kV, POLYMER TYPE, CLASS-II | RAYCHEM | - | 3 | 6
| 1 | _ | F07-01,02,03 | CAST RESIN EPOXY INSULATOR, 33kV, SIZE 100mmX300mm. | PRAGATI | _ | AS PER GA | AS PER GA
APT-SP-HE-200WATT-230V | 1 | _ | F10-01,02 | SPACE HEATER 230V AC, 200W, (FOR CABLE COMPARTMENT). | APT CONTROL | APT-SP-HE-200WATT-230V | 2 | 4
APT-SP-HE-100WATT-230V | 2 | _ | F10-03 | SPACE HEATER 230V AC, 100W, (FOR BREAKER COMPARTMENT). | APT CONTROL | APT-SP-HE-100WATT-230V | 1 | 2
APT-SP-HE-200WATT-230V | 3 | _ | F10-04 | SPACE HEATER 230V AC, 200W, (FOR PT COMPARTMENT). | APT CONTROL | APT-SP-HE-200WATT-230V | 1 | 2
APT-SP-HE-50WATT-230V | 4 | _ | F10-05 | SPACE HEATER 230V AC, 50W, (FOR BUSBAR COMPARTMENT). | APT CONTROL | APT-SP-HE-200WATT-230V | 1 | 2
| 1 | _ | F10-05 | CASTLE LOCK, 2 LOCK + 1 KEY | PATLON | _ | 1 | 2
| 2 | _ | F11-01 | PUSH BUTTON ASSEMBLY | HINDTOOLS | _ | 1 | 2
RACKING HANDLE FOR VD4 | 1 | _ | RACKING HANDLE |  |  |  | 1 | 2
PANEL-KEY | 2 | _ | PANEL KEY |  |  |  | 1 | 2

## Sheet2
MAKE LIST
SR NO. | DESCRIPTION | MAKE
1 | EARTH SWITCH | TECHNOCRAFTS
2 | BREAKER | ABB
3 | CT/PT | ECS/PRAGATI/KAPPA/GEMINI
4 | PT FUSE | PHOENIX
5 | TNC/LR SWITCH | KAYCEE/SALZER
6 | SPACE HEATER | APT CONTROLS
7 | THERMOSTAT | APT CONTROLS
8 | SWITCH BOX | PRESSFIT/ANCHOR
10 | ILLUMINATION LAMP | WIPRO/PHILIPS
11 | EM PB | L&T
12 | POWER PACK | TECHNOCRAFTS/GOGATE
13 | CONTACTOR | ABB/L&T
14 | SURGE ARRESTOR | RAYCHEM
15 | ANNUNCIATOR | GIC/ALAN/EAPL
16 | HOOTER | ALAN
17 | MCB | ABB
18 | LED LAMP | L&T
19 | METER (AMMETER/VOLTMETER) | SCHNEIDER/ELMEASURE
20 | MFM | SCHNEIDER
21 | PROT RELAY | ABB /GE /SIEMENS
22 | CRM AUX RELAY | ABB/TE
23 | CASTLE LOCK | PATLON